## Dynagage-Flow32-1K-Solar Calc
Solar Power Calculator : Flow32-1K Sap Flow System |  |  |  |  | Revised |  | Copyright © Dynamax Inc 2007
Using AVRD rev. 2.3 |  | (Dynagage sensors) |  |  | 2007-12-03 |  | Dynamax, Inc
10808 Fallstone Rd.
Power Each Sensor | [6 empty] | Suite. 350
Sensor | Watts X | Qty | = Tot W | P/V = I | I= Amperes |  | Houston, TX 77081
SGA2 | 0.05 | 0 | 0 |  |  |  | Phone: 281-564-5100
SGA3 | 0.05 | 0 | 0 |  |  |  | Fax: 281-564-5200
SGA5 | 0.08 | 0 | 0
SGA9 | 0.1 | 0 | 0
SGA10 | 0.1 | 0 | 0 |  |  |  | See insulation Chart
SGA13 | 0.15 | 0 | 0 |  |  |  | ESH Examples
SGB16 | 0.2 | 0 | 0 |  |  |  | Canada | 2.0 - 2.5
SGB19 | 0.3 | 0 | 0 |  |  |  | USA | 3.5 - 5.0
SGB25 | 0.5 | 8 | 4 |  |  |  | India | 7
SGB35 | 0.9 | 0 | 0 |  |  |  | Brazil | 4
SGB50 | 1.4 | 0 | 0 |  |  |  | Africa | 4.5 - 7.0
SGA70 | 1.6 | 0 | 0 |  |  |  | Australia | 2.5 - 5.0
SGA100 | 4 | 0 | 0 |  |  |  | Spain | 3.5
SGA150 | 10.8 | 0 | 0
| Total | 8 | 4 | 12 | 0.33333 | Amp | Solar Panel Current Out
[7 empty] | MSX60 | 3.56
Sum all sensors |  |  | Total Amps |  | 0.33333 | Amp | MSX30 | 1.75
Efficiency(80%)+Safety Factor(20%) |  |  | X1.5 |  | 0.5 | Amp | MSX20 | 1.19
24 Hr Consumption |  |  | X24 Hr |  | 12 | AHrs | MSX10 | 0.59
Consumption w/ Power Down |  |  | X15 Hr |  | 7.5 | AHrs
Enter Equivalent Sun Hours (ESH) |  |  |  | 4 | 3 | Array Current Required (24 H Oper.)
Backup Battery | 10 |  |  |  | 1.875 | Array Current Required (15 Hr Oper.)
Battery Amperage | 60 |  |  |  | Solar Panel Type Reqired - 24Hr |  |  | 3
[5 empty] | Quantity of Solar Panels Required |  |  | 0.8427
Quantity of 90 Ahr Batteries Needed |  |  |  | 2 | Solar Panel Type Required - 15Hr |  |  | 1.875
Quantity of 90 Ahr Batteries Needed |  |  |  | 1.25 | Quantity of Solar Panels Required |  |  | 0.52669
Note on C6: Enter the number of sensors by type in this column
Note on F27: Calculate The Array Current by Dividing the 24 Hr Consumption rate by the ESH.
Note on A28: Dynamax Reccommends allowing a 10 Day Battery Backup.
Note on F28: Calculate The Array Current by Dividing the 15 Hr Consumption rate by the ESH.
Note on A29: Dynamax Reccommends a 50 Ahr Deep Cycle Marine Battery or higher.
Note on F30: Quantity of Solar Panels Required at 24Hr Consumption rate
Note on A31: Quantity of 90 Ahr Batteries Needed at 24Hr Consumption Rate
Note on A32: Quantity of 90 Ahr Batteries Needed at 15Hr Consumption Rate
Note on F32: Quantity of Solar Panels Required at 15Hr Consumption rate